## Solar PV power plant
TECHNICAL DEFINITIONS |  |  | Irrigation & Miscellaneous Loads |  |  |  | ENERGY CONSUMPTION (kWh/day) | [6 empty] | Revised ENERGY CONSUMPTION (kWh/day)
Term / Abbreviation | Definition |  | Parameter | Value | Source |  | Scenario | Pump | Misc. loads | Dryer | TOTAL (kWh/day) |  |  | Scenario | Original Total (Abdoul) | + Extended Load | New TOTAL
ha | Hectare (10,000 m²) |  | Pump power | 1.5 kW | 1.5 HP Pump |  | Base | 6 | 15 | 0 | 21 |  |  | Base | 21 | 11.5 | 32.5
PSH | Peak Sun Hours: equivalent full-power sunlight hours |  | Pump operating time | 4 h | Agricultural estimate |  | 50 kg/day | 6 | 15 | 150 | 171 |  |  | 50 kg/day | 171 | 11.5 | 182.5
Derate Factor | Overall PV system losses (heat, dust, cables) |  | Miscellaneous loads | 3 kW | Various equipment |  | 200 kg/day | 6 | 15 | 600 | 621 |  |  | 200 kg/day | 621 | 11.5 | 632.5
P_h [kW] | Hydraulic power required by the pump |  | Miscellaneous load duration | 5 h | Standard farm |  | 1,000 kg/day | 6 | 15 | 3000 | 3021 |  |  | 1,000 kg/day | 3021 | 11.5 | 3032.5
P_e [kW] | Electrical power required by the pump
PV [kWp] | Peak power of the photovoltaic system |  | Mango Drying |  |  | Extended Load Inventory
MPPT | Maximum Power Point Tracking – PV efficiency optimization |  | Parameter | Value |  | Parameter | Value | Source
Smart add-ons | Sensors, IoT, PLCs, GSM/Wi-Fi monitoring |  | Energy efficiency of drying | 3 kWh/kg of fresh mango |  | Storage/Cooling | 8 kWh/day | Crop storage refrigeration
DoD | Depth of Discharge – battery discharge depth |  | Production Scenario 1 | 50 kg/day |  | Lighting | 2 kWh/day | Buildings + night security
BOS | Balance of System – structure, cables, protections |  | Production Scenario 2 | 200 kg/day |  | Security (fencing/cameras) | 1 kWh/day | Perimeter monitoring
LCOE | Levelized Cost of Energy – real energy cost |  | Production Scenario 3 | 1,000 kg/day |  | Monitoring/IoT | 0.5 kWh/day | Sensors, GSM/Wi-Fi
[6 empty] | TOTAL additional load | 11.5 kWh/day
Solar Parameters |  |  |  | Battery Parameters
Parameter | Value | Notes |  | Parameter | Value
PSH Burkina Faso | 5.5 h |  |  | Battery type | Lithium-ion
Tracker gain | 20% |  |  | DoD | 80%
Effective PSH | 6.6 h |  |  | Inverter efficiency | 90%
Loss factor | 25% |  |  | Desired autonomy | 8 h
Derate factor | 0.75
Average area per kWp | 8.5 m² | Trackers
Complete PV System | [9 empty] | Revised PV Sizing
Item | Value |  | Scenario | Energy (kWh/day) | PV required (kWp) | No. of 400W panels | Area m² | Area ha |  | Scenario | Energy (kWh/day) | PV required (kWp) | No. of 400W panels | Area (m²) | Area (ha)
Required PV = Energy / (PSH × Derate) | PV = kWh / 4.95 |  | Base | 21 | 4.24 | 11 | 36 | 0.004 |  | Base | 32.5 | 6.57 | 17 | 55.9 | 0.0056
|  |  | 50 kg/day | 171 | 34.55 | 87 | 294 | 0.029 |  | 50 kg/day | 182.5 | 36.87 | 93 | 313.4 | 0.0313
|  |  | 200 kg/day | 621 | 125.45 | 314 | 1066 | 0.107 |  | 200 kg/day | 632.5 | 127.78 | 320 | 1086.1 | 0.1086
|  |  | 1,000 kg/day | 3021 | 610.3 | 1526 | 5188 | 0.519 |  | 1,000 kg/day | 3032.5 | 612.63 | 1532 | 5207.4 | 0.5207
BATTERY SIZING
Parameter | Formula |  | Scenario | Energy / 8h (kWh) | With losses (kWh) | Nominal capacity (kWh) |  |  |  |  | Revised BATTERY SIZING
Energy 8h = (kWh/day ÷ 24) × 8 | Usable energy |  | Base | 7 | 7.78 | 9.72 |  |  |  | Scenario | Energy/8h (kWh) | With losses (kWh) | Nominal capacity (kWh)
Energy with losses = usable ÷ 0.9 | Actual required energy |  | 50 kg/day | 57 | 63.33 | 79.17 |  |  |  | Base | 10.83 | 12.04 | 15.05
Total capacity = actual ÷ DoD | Final battery capacity (kWh) |  | 200 kg/day | 207 | 230 | 287.5 |  |  |  | 50 kg/day | 60.83 | 67.59 | 84.49
|  |  | 1,000 kg/day | 1007 | 1118.89 | 1398.61 |  |  |  | 200 kg/day | 210.83 | 234.26 | 292.82
[10 empty] | 1,000 kg/day | 1010.83 | 1123.15 | 1403.94
COSTS (CAPEX)
Component | Price |  | Scenario | PV cost ($) | Battery ($) | Inverter ($) | Total CAPEX ($) |  |  | Revised CAPEX (PV + Battery)
PV + BOS | $1.20/W |  | Base | 5088 | 3888 | 4500 | 13476 |  |  | Scenario | PV cost ($) | Battery ($) | Subtotal (excl. inverter)
Li-Ion Battery | $400/kWh |  | 50 kg/day | 41460 | 31668 | 30000 | 103128 |  |  | Base | 7884 | 6020 | 13904
Inverter | $1,000/kW |  | 200 kg/day | 150540 | 115000 | 110000 | 375540 |  |  | 50 kg/day | 44244 | 33796 | 78040
|  |  | 1,000 kg/day | 732360 | 559444 | 540000 | 1831804 |  |  | 200 kg/day | 153336 | 117128 | 270464
[10 empty] | 1,000 kg/day | 735156 | 561576 | 1296732
ROI (Return on Investment)
Parameter | Value |  | Scenario | Savings/day ($) | Savings/year ($) | Maintenance ($) | Net savings/year ($) | Payback (yrs)
Diesel LCOE | $0.40/kWh |  | Base | 8.4 | 3066 | 270 | 2796 | 4.82
Days/year | 365 |  | 50 kg/day | 68.4 | 24966 | 2063 | 22903 | 4.5
Maintenance | 2% of CAPEX |  | 200 kg/day | 248.4 | 90666 | 7511 | 83155 | 4.52
|  |  | 1,000 kg/day | 1208.4 | 441066 | 36636 | 404430 | 4.53
Carbon Footprint Calculator
Parameter | Value | Comment |  | Scenario | Annual Production (kWh/yr) | PV Emissions (kg CO₂/yr) | Grid Equivalent (kg CO₂/yr) | + Generator (kg CO₂/yr) | Total System Emissions | Reduction vs Grid
PV Lifecycle Emission Factor | 0,05 kg CO₂/kWh | Average lifecycle emissions of PV |  | Base | 11862.5 | 593.1 | 5931.3 | 1080 | 1673.1 | 71.8%
Grid Emission Factor | 0,5 kg CO₂/kWh | Conventional grid equivalent |  | 50 kg/day | 66612.5 | 3330.6 | 33306.3 | 1080 | 4410.6 | 86.8%
Generator Emission Factor | 0,75 kg CO₂/kWh | From Section 6 |  | 200 kg/day | 230862.5 | 11543.1 | 115431.3 | 1080 | 12623.1 | 89.1%
|  |  |  | 1,000 kg/day | 1106862.5 | 55343.1 | 553431.3 | 1080 | 56423.1 | 89.8%
Monitoring Specifications
Screen | Content
Dashboard | Production solaire du jour (kWh), % autoconsommation
Consumption | Répartition temps réel par poste (pompe, divers, stockage, éclairage, sécurité, séchoir)
Generator | Statut, heures cumulées, niveau fuel, coût cumulé
Carbon | CO₂ évité cumulé (repris de la Section 7)
Alerts | Panneau défaillant, batterie faible, activation générateur, coupure réseau
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: is this a small pump? would it be enough for the farm? Reply: Just for the scenario
Note on C5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: why did you assume that the pump is needed only for 4 hours?
Note on B8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: what is meant by Misc?? Reply: used for Miscellaneous load
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: what does PSH stands for? could you explain? Reply: Peak Sun Hours: equivalent full-power sunlight hours
Note on B15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: what is meant by Derate? Reply: Overall PV system losses (heat, dust, cables)
Note on B33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: please add the costs calculations

## Solar & Energy Systems
Scenario | Daily Energy (kWh/day) | Required PV Array (kWp) | Number of 400 W Panels | Required Battery (usable kWh) | Inverter Size (kW, nominal)
Small farm (≈2 ha) | 37 | 7.5 | 19 | 52 | 6.3
TABLE1: Farm Scenario
Parameter | Metric | Value | Comment
Scenario | Description | Small farm (≈2 ha) | Fixed base
Daily Energy | kWh/day | 37 | Total daily consumption
Required PV Array | kWp | 7.5 | Fixed-tilt system
Required PV Array | kWp | 6 | With tracking
400 W Panels | Units | 19 | Fixed-tilt
400 W Panels | Units | 15 | Tracking
Battery | Usable kWh | 52 | Storage requirement
Inverter Size | kW | 6.3 | Nominal rating
TABLE 2 : Calculation Summary
Parameter | Metric | Value | Comment
Daily Energy | kWh/day | 37 | Same for both systems
PV Power (Fixed-Tilt) | kWp | 7.6 | Baseline
PV Power (Tracking) | kWp | 6 | 20% reduction
Panels (Fixed-Tilt) | Units | 19 | 0.4 kW each
Panels (Tracking) | Units | 15 | 0.4 KW each
System Cost (Fixed-Tilt) | € | 43825 | Total system cost
System Cost (Tracking) | € | 42850 | Lower due to fewer panels
Payback Period (Fixed-Tilt) | Years | 32 | =Cost/Savings
Payback Period (Tracking) | Years | 31 | =Cost/Savings
Annual Savings | €/year | 1351 | =Annual production×rate
TABLE 3: Energy Breakdown (37 kWh/day)
Parameter | Metric | Value | Comment
Irrigation | kWh/day | 17 | Efficient pumps
Ventilation/Greenhouses | kWh/day | 7 | Climate control
Storage/Cooling | kWh/day | 5 | Refrigeration
Tools/Machinery | kWh/day | 4 | Farm tools
Electric Fences | kWh/day | 2 | Protection system
Office/Management | kWh/day | 2 | Monitoring
Total | kWh/day | 37 | Optimized consumption
TABLE 4 :System Size and Explanation
Parameter | Metric | Value | Comment
PV Size (Fixed-Tilt) | kWp | 7.6 | 19 panels × 0.4 kW
PV Size (Tracking) | kWp | 6 | 15 panels × 0.4 kW
Tracking Gain | % | 30 | Higher solar yield
Panel Reduction | % | -20 | Fewer panels needed
TABLE 5 : Cost Breakdown
Parameter | Metric | Value | Comment
PV Panels (Fixed-Tilt) | € | 9000 | Unit price: 1200 €/kWp
PV Panels (Tracking) | € | 7200 | Lower due to fewer panels
Tracking Hardware | € | 3000 | Only for tracking
Mounting/Installation (Fixed-Tilt) | € | 10875 | Estimated total
Mounting/Installation (Tracking) | € | 8700 | Lower due to fewer panels
Battery | € | 20800 | 52 kWh usable with 400€/KWh
Inverter | € | 3150 | 6.3 kW nominal with 500€/KW
Total Cost (Fixed-Tilt) | € | 43825 | System total
Total Cost (Tracking) | € | 42850 | System total
Cost Difference | € | -975 | Tracking cheaper overall
TABLE 6 : ROI Calculation
Parameter | Metric | Value | Comment
Annual Production | kWh/year | 13505 | Formula: 37 × 365
Electricity Price | €/kWh | 0.1 | Agricultural tariff
Annual Savings | €/year | 1351 | Production × rate
System Cost (Fixed-Tilt) | € | 43825 | Reference cost table
System Cost (Tracking) | € | 42850 | Reference cost table
Payback (Fixed-Tilt) | Years | 32 | Cost ÷ savings
Payback (Tracking) | Years | 31 | Cost ÷ savings
TABLE 7 : Optimization Tip
Parameter | Metric | value | Comment
Irrigation Shift | %Daytime | 50 | Reduces battery need
New Battery Size | kWh | 30 | Updated storage requirement
New Payback | Years | 26 | Lower CAPEX
TABLE 8: Recommendations and Data Alignment
Parameter | Metric | Value | Comment
Data Alignment | — | Consistent | Same 37 kWh/day used in all tables
Energy Need Definition | kWh/day | 37 | Basis for sizing PV and battery
Panel Selection:monocrystalline or polycrystalline | W | 400 | Monocrystalline: best efficiency ideal in moderate temperatures or well-ventilated areas. Polycrystalline: better thermal tolerance, recommended for hot climates like in the Sahel.
PV Configuration(Tracking) | kWp | 6 | 20% fewer panels, same output
Battery Optimization | kWh | 30 | Shift 50% irrigation to daytime to reduce capacity
Estimated carbon factor | kg CO₂/kWh | 0.05 | Average life-cycle emissions of PV panels
Carbon Footprint | kg CO₂/year | 675.25 | Life-cycle emissions from PV generation
Grid Emission Comparison | kg CO₂/year | 6752.5 | Conventional power equivalent (0.5 kg CO₂/kWh)
Emission Reduction | % | 90 | Compared to grid-based electricity
Monitoring System | IoT-based | Recommended | Enables tracking of energy use and CO₂ savings
Overall Recommendation | no metric | Adopt tracking PV with reduced battery | Improves efficiency, lowers CAPEX and emissions
TABLE 9: Generator Backup Sizing
Parameter | Metric | Value | Comment
Critical loads to be supplied | kWh/day | 9 | Storage/Cooling + Fences + Office/Monitoring
Generator Size | kW | 8 | Covers full farm, aligned with 6.3 kW inverter
Diesel Cost | €/kWh | 0.40 | Same assumption as Abdoul's LCOE
Annual Usage Hours | h/year | 180 | ~5 outages/month × 3h estimate
Annual Energy from Generator | kWh/year | 1440 | 8 kW × 180 h
Annual Generator Cost | €/year | 576 | 1 440 kWh × 0,40 €/kWh
Generator Emission Factor | kg CO₂/kWh | 0.75 | Standard diesel generator factor
Generator Annual Emissions | kg CO₂/year | 1080 | 1 440 kWh × 0,75
Generator CAPEX (8 kW) | € | 4000 | Estimate at ~500 €/kW installed
Generator Payback vs. full diesel | Years
TABLE 10: Solar Panel Monitoring
App Screen | Content
Dashboard | Daily solar energy production (kWh), self-consumption rate (%)
Consumption | Real-time energy consumption breakdown by load category (based on Table 3)
Generator | Generator status, cumulative operating hours, fuel level
Carbon | Cumulative CO₂ emissions avoided (updated from Table 8)
Alerts | Faulty panel, low battery level, grid power outage

## Energy Systems
Technical Definitions
Term / Abbreviation | Definition
ha | Hectare (10,000 m²)
PSH | Peak Sun Hours: equivalent full-power sunlight hours | [8 empty] | Base Load Inventory (Abdoul ) |  |  | Extended Load Inventory (Aida ) |  |  | Revised ENERGY CONSUMPTION (kWh/day)
Derate Factor | Overall PV system losses (heat, dust, cables) | [8 empty] | Parameter | Value | Source | Parameter | Value | Source | Scenario | Original Total (Abdoul) | + Extended Load | New TOTAL
P_h [kW] | Hydraulic power required by the pump | [8 empty] | Pump power | 1.5 kW | 1.5 HP Pump | Storage/Cooling | 8 kWh/day | Crop storage refrigeration | Base | 21 | 11.5 | 32.5
P_e [kW] | Electrical power required by the pump | [8 empty] | Pump operating time | 4 h | Agricultural estimate | Lighting | 2 kWh/day | Buildings + night security | 50 kg/day | 171 | 11.5 | 182.5
PV [kWp] | Peak power of the photovoltaic system | [8 empty] | Miscellaneous loads | 3 kW | Various equipment | Security (fencing/cameras) | 1 kWh/day | Perimeter monitoring | 200 kg/day | 621 | 11.5 | 632.5
MPPT | Maximum Power Point Tracking – PV efficiency optimization | [8 empty] | Miscellaneous load duration | 5 h | Standard farm | Monitoring/IoT | 0.5 kWh/day | Sensors, GSM/Wi-Fi | 1,000 kg/day | 3021 | 11.5 | 3032.5
Smart add-ons | Sensors, IoT, PLCs, GSM/Wi-Fi monitoring | [11 empty] | TOTAL extended load | 11.5 kWh/day
DoD | Depth of Discharge – battery discharge depth
BOS | Balance of System – structure, cables, protections | [8 empty] | Mango Drying (Abdoul)
LCOE | Levelized Cost of Energy – real energy cost | [8 empty] | Parameter | Value
[10 empty] | Energy efficiency of drying | 3 kWh/kg of fresh mango
[10 empty] | Production Scenario 1 | 50 kg/day
[10 empty] | Production Scenario 2 | 200 kg/day
[10 empty] | Production Scenario 3 | 1,000 kg/day
Solar Parameters ( Abdoul)
Parameter | Value | Notes | [7 empty] | Battery Parameters(Abdoul)
PSH Burkina Faso | 5.5 h | [8 empty] | Parameter | Value
Tracker gain | 20% | [8 empty] | Battery type | Lithium-ion
Effective PSH | 6.6 h | [8 empty] | DoD | 80%
Loss factor | 25% | [8 empty] | Inverter efficiency | 90%
Derate factor | 0.75 | [8 empty] | Desired autonomy | 8 h
Average area per kWp | 8.5 m² | Trackers
Complete PV System
Item | Value |  | Revised PV Sizing
Required PV = Energy / (PSH × Derate) | PV = kWh / 4.95 |  | Scenario | Energy (kWh/day) | PV required (kWp) | No. of 400W panels | Area (m²) | Area (ha)
|  |  | Base | 32.5 | 6.57 | 17 | 55.9 | 0.0056
|  |  | 50 kg/day | 182.5 | 36.87 | 93 | 313.4 | 0.0313
|  |  | 200 kg/day | 632.5 | 127.78 | 320 | 1086.1 | 0.1086
|  |  | 1,000 kg/day | 3032.5 | 612.63 | 1532 | 5207.4 | 0.5207
BATTERY SIZING
Parameter | Formula |  |  |  | Revised BATTERY SIZING
Energy 8h = (kWh/day ÷ 24) × 8 | Usable energy |  |  | Scenario | Energy/8h (kWh) | With losses (kWh) | Nominal capacity (kWh)
Energy with losses = usable ÷ 0.9 | Actual required energy |  |  | Base | 10.83 | 12.04 | 15.05
Total capacity = actual ÷ DoD | Final battery capacity (kWh) |  |  | 50 kg/day | 60.83 | 67.59 | 84.49
|  |  |  | 200 kg/day | 210.83 | 234.26 | 292.82
|  |  |  | 1,000 kg/day | 1010.83 | 1123.15 | 1403.94
COSTS (CAPEX)
Component | Price |  |  | Revised CAPEX (PV + Battery)
PV + BOS | $1.20/W |  |  | Scenario | PV cost ($) | Battery ($) | Subtotal (excl. inverter)
Li-Ion Battery | $400/kWh |  |  | Base | 7884 | 6020 | 13904
Inverter | $1,000/kW |  |  | 50 kg/day | 44244 | 33796 | 78040
|  |  |  | 200 kg/day | 153336 | 117128 | 270464
|  |  |  | 1,000 kg/day | 735156 | 561576 | 1296732
TRACKING COMPARISON REVISED( Base Narcisse)
Parameter | Fixed-Tilt | Tracking | Comment
PV Power | 7,6 kWp | 6,0 kWp | 20% reduction (valeur unifiée)
Panels | 19 | 15 | 0.4 kW each
System Cost | 43825 | 42850 | Tracking cheaper overall
Panel type recommended | — | Polycrystalline | Better thermal tolerance for Sahel climate
GENERATOR BACKUP SIZING
Parameter | Value | Comment
Critical Load | 9,5 kWh/day | Storage/Cooling + Security + Monitoring
Generator Size | 8 kW | Covers critical loads + margin
Diesel Cost | 0,40 $/kWh | Same as Abdoul's LCOE assumption
Annual Usage Hours | 180 h/year | Estimated backup usage
Annual Energy from Generator | 1 440 kWh/year | 8 kW × 180 h
Annual Generator Cost | 576 $/year | 1 440 × 0,40
Generator Emission Factor | 0,75 kg CO₂/kWh | Standard diesel generator
Generator Annual Emissions | 1 080 kg CO₂/year | 1 440 × 0,75
Generator CAPEX | 4 000 $ | Estimate at $500/kW installed
CARBON FOOTPRINT CALCULATOR
Parameter | Value | Comment |  | Scenario | Annual Production (kWh/yr) | PV Emissions (kg CO₂/yr) | Grid Equivalent (kg CO₂/yr) | + Generator (kg CO₂/yr) | Total System Emissions | Reduction vs Grid
PV Lifecycle Emission Factor | 0,05 kg CO₂/kWh | Average lifecycle emissions of PV |  | Base | 11862.5 | 593.1 | 5931.3 | 1080 | 1673.1 | 71.8%
Grid Emission Factor | 0,5 kg CO₂/kWh | Conventional grid equivalent |  | 50 kg/day | 66612.5 | 3330.6 | 33306.3 | 1080 | 4410.6 | 86.8%
Generator Emission Factor | 0,75 kg CO₂/kWh | From Section 6 |  | 200 kg/day | 230862.5 | 11543.1 | 115431.3 | 1080 | 12623.1 | 89.1%
|  |  |  | 1,000 kg/day | 1106862.5 | 55343.1 | 553431.3 | 1080 | 56423.1 | 89.8%
MONITORING APP SPECIFICATION
Screen | Content
Dashboard | Daily solar production (kWh), % self-consumption
Consumption | Real-time breakdown by system (pump, miscellaneous, storage, lighting, security, dryer)
Generator | Status, cumulative hours, fuel level, cumulative cost
Carbon | Cumulative CO₂ avoided (from Section 7)
Alerts | Panel failure, low battery, generator activation, grid outage
Note on B44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: please add the costs calculations

## ENERGY SYSTEM SUMMARY
ASSUMPTIONS
PSH Burkina Faso | Diesel Cost (LCOE) | Grid Emission Factor
6.6 hours (actual, with tracking) | 0,40 $/kWh | 0,5 kg CO₂/kWh
ANNUAL BENEFITS — SCENARIO "50 kg/day"
Benefit type | Amount | Details
Diesel savings avoided (solar) | 24 966 $/an | vs. Equivalent diesel generation
Maintenance cost | − 2 063 $/an | 2% of CAPEX
Generator backup cost | − 576 $/an | 180h/an of estimated backup
NET SAVINGS | 22 327 $/an
Estimated payback | ~4,7 ans | Based on avoided diesel costs
CARBON IMPACT — SCENARIO "50 kg/day"
Benefit type | Amount | Details
Emissions avoided vs. grid | 33 306 kg CO₂/year | Solar vs. equivalent conventional grid
Residual emissions (PV + generator) | 4 411 kg CO₂/year | PV lifecycle + diesel backup
NET REDUCTION | 86.8% | Compared to 100% grid/diesel power

## TEAM SUMMARY — Energy System
Extended Load Inventory
Parameter | Value | Source
Pump power | 1.5 kW | Abdoul (base)
Pump operating time | 5 h (corrected, was 4h) | Water Supply 2026 , validated by real data (20 m³/day ÷ 4 m³/h)
Miscellaneous loads | 3 kW × 5h | Abdoul (base)
Storage/Cooling | 8 kWh/day | Aida (new)
Lighting | 2 kWh/day | Aida (new)
Security (fencing/cameras) | 1 kWh/day | Aida (new)
Monitoring/IoT | 0.5 kWh/day | Aida (new)
TOTAL extended load | 11.5 kWh/day
Energy Consumption (Revised)
Scenario | Pump (corrected) | Misc. | Extended (Aida) | Dryer | TOTAL (kWh/day)
Base | 7.5 | 15 | 11.5 | 0 | 34.0
50 kg/day | 7.5 | 15 | 11.5 | 150 | 184.0
200 kg/day | 7.5 | 15 | 11.5 | 600 | 634.0
1,000 kg/day | 7.5 | 15 | 11.5 | 3 | 3,034.0
PV Sizing (Revised)
Scenario | Energy (kWh/day) | PV required (kWp) | No. of 400W panels | Area (m²) | Area (ha)
Base | 34.0 | 6.87 | 18 | 58.4 | 0.0058
50 kg/day | 184.0 | 37.17 | 93 | 316.0 | 0.0316
200 kg/day | 634.0 | 128.08 | 321 | 1,088.7 | 0.1089
1,000 kg/day | 3,034.0 | 613.13 | 1.533 | 5,211.6 | 0.5212
Battery Sizing (Revised)
Scenario | Energy/8h (kWh) | With losses (kWh) | Nominal capacity (kWh)
Base | 11.33 | 12.59 | 15.74
50 kg/day | 61.33 | 68.15 | 85.19
200 kg/day | 211.33 | 234.81 | 293.52
1,000 kg/day | 1,011.33 | 1,123.70 | 1,404.63
CAPEX (Revised)
Scenario | PV cost ($) | Battery ($) | Subtotal (excl. inverter)
Base | 8.244 | 6.296 | 14.54
50 kg/day | 44.604 | 34.076 | 78.68
200 kg/day | 153.696 | 117.408 | 271.104
1,000 kg/day | 735.756 | 561.852 | 1,297,608
Tracking Comparison (Revised)
Parameter | Fixed-Tilt | Tracking | Comment
PV Power | 6.98 kWp | 5.51 kWp | 20% fewer panels
Panels | 17 | 14
System Cost | ~40,275 | ~39,380 | Tracking remains cheaper
Annual Production | 12,410 kWh/yr | 12,410 kWh/yr | Base 34 kWh/day × 365
Annual Savings (at 0.40 $/kWh) | 4,964 $/yr | 4,964 $/yr
Payback | ~8.1 years | ~7.9 years | Consistent with overall ROI calculation
Generator Backup Sizing (added)
Parameter | Value | Comment
Critical Load | 9.5 kWh/day | Storage/Cooling + Security + Monitoring
Generator Size | 8 kW
Annual Usage | 180 h/year
Annual Cost | 576 $/year
Annual Emissions | 1,080 kg CO₂/year
Carbon Footprint Calculator (added)
Scenario | Annual Production (kWh/yr) | PV Emissions (kg CO₂/yr) | Grid Equivalent (kg CO₂/yr) | + Generator | Total Emissions | Reduction vs Grid
Base | 12.41 | 620.5 | 6.205 | 1.08 | 1,700.5 | 72.6% (vs 71.8% before)
50 kg/day | 67.16 | 3.358 | 33.58 | 1.08 | 4.438 | 86.8%
200 kg/day | 231.41 | 11,570.5 | 115.705 | 1.08 | 12,650.5 | 89.1%
1,000 kg/day | 1,107,410 | 55,370.5 | 553.705 | 1.08 | 56,450.5 | 89.
CO₂ per kg dried mango (for connection SANON — Product Transformation):
Scenario | Dried Output (kg/day) | CO₂/kg dried mango
50 kg/day | 16.5 | 0.737
200 kg/day | 66 | 0.525
1,000 kg/day | 330 | 0.469